## Slide 1: FUNDAMENTALS OF WATER AND WASTEWATER TREATMENT
Summer 2020

## Slide 2: Why do we treat water?
To prevent the transmission of diseases and consumption of chemically-unsafe water
  https://www.epa.gov/ground-water-and-drinking-water/national-primary-drinking-water-regulations
Aesthetically appealing
Non-corrosive and non-scaling to infrastructure

## Slide 3: Why do we treat wastewater?
To prevent the transmission of diseases
To protect receiving environments
  and downstream users (water rights…)
To enable water reuse
  Non-potable reuse
  Indirect potable reuse
  Direct potable reuse

## Slide 4: History of Water Treatment and Regulations
Ancient civilizations established around water sources – quantity and quality
Water treatment originally focused on improving aesthetic qualities of water
During the mid to late 1800s, scientists gained a greater understanding of sources and effects of drinking water contaminants, especially those that were not visible to naked eye
In 1908, chlorine was used for the first time as a primary disinfectant of drinking water in Jersey City, New Jersey
In 1914, the U.S. Public Health Service sets standards for the bacteriological quality of drinking water
Safe Drinking Water Act of 1974 – MCLs
Regulations stem from bad past experiences and from research

## Slide 5: Challenges in Water Treatment
Water analysis – quantity and quality…
  How clean is clean?
Each source is different and requires different approach
The quality (and capacity) of source water can change seasonally or gradually – how do we plan ahead?
Response to demand
Alternative resources / reuse / desalination

## Slide 6: Sources of Water that Require Treatment
Surface (rivers, lakes, reservoirs)
Groundwater (fresh, brackish, under-the-influence)
Seawater
Domestic wastewater
Industrial wastewater

## Slide 7: Typical concentrations of common water constituents in different water sources

## Slide 8: Industrial Wastewater

## Slide 9: Typical Characteristics of Untreated Municipal WW in the US

## Slide 10: Possible Levels of Pathogens in WW
Type of pathogen |  | Possible concentration per liter in municipal wastewater1
Viruses: | Enteroviruses2 | 5,000
Bacteria: | Pathogenic E. coli3 | Uncertain?
 | Salmonella spp. | 7,000
 | Shigella spp. | 7,000
 | Vibrio cholerae | 1,000
Protozoa: | Entamoeba histolytica | 4,500
Helminths: | Ascaris Lumbricoides | 600
 | Hookworms4 | 32
 | Schistosoma mansoni | 1
 | Taenia saginata | 10
 | Trichuris trichiura | 120
1 Based on 100 LPCD of municipal sewage and 90% inactivation of excreted pathogens 2 Includes polio-, echo- and coxsackieviruses 3 Includes enterotoxigenic, enteroinvasive and enteropathogenic E. coli 4 Anglostoma duedenale and Necator americanus
Source: Feachem et al. (1983)

## Slide 11: Variation in Water Quality (example from surface water)

## Slide 12: Mechanisms in Water and Wastewater Treatment
Removal
Addition
Transformations
Fate
Dissolved chemical (organic/inorganic)
Colloids
Particles
Gases
Microorganisms
of

## Slide 13: Treatment Processes for Drinking Water Include:
Particulate removal:
Coagulation/Flocculation
Sedimentation
Flotation
Filtration
Membranes
Advanced processes:
Oxidation/Reduction
Precipitation
Ion exchange
RO membranes
Biological treatment
Softening
Adsorption
Gas addition or removal:
Aeration
Stripping
Pathogens removal:
Disinfection

## Slide 14: Overlap with Wastewater Treatment Processes:
Particulate removal:
Coagulation/Flocculation
Sedimentation
Flotation
Filtration
Membranes
Advanced processes:
Oxidation/Reduction
Precipitation
Ion exchange
RO membranes
Biological treatment
Softening
Adsorption
Gas addition or removal:
Aeration
Stripping
Pathogens removal:
Disinfection

## Slide 15: Projects this summer…
Particulate removal:
Coagulation/Flocculation
Sedimentation
Flotation
Filtration
Membranes
Advanced processes:
Oxidation/Reduction
Precipitation
Ion exchange
RO membranes
Biological treatment
Softening
Adsorption
Gas addition or removal:
Aeration
Stripping
Pathogens removal:
Disinfection

## Slide 16: Water and Wastewater Treatment: Common Elements
Multiple unit processes and unit operations
Consideration of hydraulic and watershed issues
Skill overlap for professionals

## Slide 17: Water and Wastewater Treatment: Differences
Different receptors – risk assessment
Different perspective on pollutants (e.g., organics) and concentrations
Different standards that govern design of facilities
Different legislation

## Slide 19: Conventional Water Treatment Train
https://www.youtube.com/watch?v=9z14l51ISwg

## Slide 20: Coagulation

## Slide 21: Destabilization and Restabilization

## Slide 22: Coagulating Power of Inorganic Electrolytes

## Slide 23: Coagulation in Wastewater Treatment
Used mainly for removal of phosphorus (phosphate)
Multivalent ions are used (Ca (from lime), Al, Fe)
10Ca2+ + 6PO43− + 2OH−  Ca10(PO4)6(OH)2
Hydroxyapatite
Al3+ + HnPO43−  AlPO4 + nH+
Fe3+ + HnPO43−  FePO4 + nH+
Competition/coprecipitation

## Slide 24: Mixed-Media Filter
anthracite coal (1.55), quartz sand (2.65), garnet (4.05)

## Slide 25: Filters Classified by Driving Force
Gravity filters:
2-3 m head
housed in open concrete or steel tanks
large and small systems
Pressure filters:
higher head
housed in closed steel vessels
costly; small systems

## Slide 27: Rapid Filtration – Filter Run
Effluent turbidity characterized by three distinct segments:
Ripening
  media conditioning (15 min - 2 hr)
  Sometimes contain two peaks
  Size and duration can be reduced by proper backwashing procedure
  Filter-to-waste line
Effective filtration
  Steady state with turbidity <0.1 NTU
  Gradual increasing in head loss
Breakthrough
  Filter bed can’t hold more particles
  Effluent turbidity increases
  Headloss increases

## Slide 28: Rapid Filtration – End of Filter Run
Can be triggered by several events and lead to backwash:
Breakthrough
  Preventing high-turbidity water from entering the distribution system
Headloss
  Increases beyond the available head through the process
  Rapid filters are typically designed with 1.8 - 3 m (6 - 10 ft) available head
  If in specific cases neither are reached within several days: utility initiate backwash after a set period of time

## Slide 29: Conventional Wastewater Treatment Plant
http://www.youtube.com/watch?v=ZSFdOjxB-1I

## Slide 30: Types of Wastewater Treatment Plants
Primary Treatment Removal
25-50% of the incoming BOD5
50-70% of the TSS
~65% of the oil and grease
Secondary Treatment Removal
Further treatment of primary
Removal of biodegradable dissolved and colloidal organic matter
High-rate biological treatment typically remove 85 % of the BOD5 and TSS
Tertiary Treatment Removal
Specific constituents that cannot be removed by secondary treatment
Individual processes necessary to remove N, P, TSS, refractory organics, heavy metals, and dissolved solids
https://www.yakimawa.gov/services/wastewater-treatment-plant/operations-maintenance/

## Slide 31: Types of Wastewater Treatment Plants
Primary Treatment
  Removal of settleable organic and inorganic solids by sedimentation, and the removal of materials that will float (scum) by skimming
  25 to 50% of the incoming biochemical oxygen demand (BOD5), 50 to 70% of the total suspended solids (SS), and ~65% of the oil and grease are removed during primary treatment

## Slide 32: Types of Wastewater Treatment Plants
Secondary Treatment
  Further treatment of the effluent from primary treatment
  Removal of biodegradable dissolved and colloidal organic matter using aerobic biological treatment processes
  Treatment is performed in the presence of oxygen by aerobic microorganisms that metabolize organic matter in the wastewater  producing more microorganisms and inorganic end-products (CO2, NH3, and H2O)
  Activated sludge processes, trickling filters or biofilters, oxidation ditches, and rotating biological contactors (RBC)
  High-rate biological treatment processes, in combination with primary sedimentation, typically remove 85 % of the BOD5 and SS originally present in the raw WW and some of the heavy metals

## Slide 33: Types of Wastewater Treatment Plants
Tertiary / Advanced Treatment
  Employed when specific wastewater constituents that cannot be removed by secondary treatment must be removed
  Individual treatment processes are necessary to remove nitrogen, phosphorus, additional suspended solids, refractory organics, heavy metals, and dissolved solids

## Slide 34: Contaminant Removal Effectiveness
Process | Suspended solids | Dissolved organics | Dissolved inorganics | Micro-organisms | Dissolved gases
Biological Processes |  |  |  |  | 
Activated sludge | X | X | -- | X | --
Anaerobic digester | X | X | -- | -- | --
Bio-filters | -- | X | -- | -- | --
Extended aeration |  |  |  |  | 
Bio-denitrification | -- | L | -- | -- | --
Bio-nitrification | X | X | -- | -- | --
Oxidation ditch | X | X | -- | X | --

## Slide 35: Contaminant Removal Effectiveness
Process | Suspended solids | Dissolved organics | Dissolved inorganics | Micro-organisms | Dissolved gases
Chemical Processes |  |  |  |  | 
Chemical oxidation |  |  |  |  | 
Catalytic oxidation | X | X | -- | X | X
Chlorination | X | X | -- | X | --
Ozonation | -- | L | -- | X | X
Wet oxidation | X | X | -- | X | X
Chemical precipitation | -- | -- | X | -- | --
Chemical reduction | -- | -- | X | -- | --
Coagulation |  |  |  |  | 
inorganic chemicals | X | X | -- | X | --
polyelectrolytes | X | X | -- | X | --
Disinfection | -- | -- | -- | X | --

## Slide 36: Contaminant Removal Effectiveness
Process | Suspended solids | Dissolved organics | Dissolved inorganics | Micro-organisms | Dissolved gases
Chemical Processes |  |  |  |  | 
Electrolytic processes |  |  |  |  | 
Electrodialysis | -- | -- | X | -- | --
Electrolysis | -- | -- | X | -- | --
Extractions |  |  |  |  | 
Ion exchange | -- | -- | X | -- | --
Liquid-liquid (solvent) | -- | -- | X | -- | --
Incineration | X | X | -- | X | X

## Slide 37: Contaminant Removal Effectiveness
Process | Suspended solids | Dissolved organics | Dissolved inorganics | Micro-organisms | Dissolved gases
Physical Processes |  |  |  |  | 
Carbon adsorption |  |  |  |  | 
Granular activated | X | X | -- | -- | X
Powdered | X | X | -- | X | X
Distillation | X | X | X | X | --
Filtration |  |  |  |  | 
Diatomaceous earth filtration | X | -- | -- | X | --
Dual media | X | -- | -- | X | --
Micro-screening | X | -- | -- | X | --
Sand filtration | X | -- | -- | X | --
Flocculation-sedimentation | X | -- | -- | X | --
Foam separation | X | -- | X | -- | --
Freezing | -- | X | X | -- | --

## Slide 38: Contaminant Removal Effectiveness
Process | Suspended solids | Dissolved organics | Dissolved inorganics | Micro-organisms | Dissolved gases
Membrane processes |  |  |  |  | 
Microfiltration | X | -- | -- | X | --
Ultrafiltration | X | X | -- | X | --
Nanofiltration | X | X | X | X | --
Reverse osmosis | X | X | X | X | --
Stripping (air or steam) | X | X | -- | -- | X

## Slide 39: Membrane Separation
Solvent
Particle or Solute Molecule
Membrane
Permeate
Feed
Notes: Membrane processes are used in water treatment for solid/liquid separation. RO and NF are pressure-driven membrane processes. In this figure, the orange circles represent the particles or solute molecules and the blue circles represents the solvent (water). The feed solution is forced under pressure through the membrane (animate) and the result is a relatively clean permeate solution.
Separation occurs because the membrane transports one component (the water) more readily than any other components.

## Slide 40: Pressure-driven Membrane Processes

## Slide 41: Selection of Membrane Processes
‘loose’ and ‘tight’

## Slide 42: Material Balance in Membrane Separation
Mass balance for water flow
Qf = Qc + Qp
Mass balance for solute flux
QfCf = QcCc + QpCp
Product recovery
r = (Qp/Qf)·100%
Solute rejection
  rej = (Cf-Cp)/Cf * 100%
  = (1-Cp/Cf) * 100%
Power consumption:
Ė = Qf * Pf (W)
SE = Ė/Qp (kWh/m3)

## Slide 44: Pathogen Reduction Goals vs. Credits for Direct Potable Reuse
GOALS
 | Ozone | BAF | UF | GAC | UV | Cl2 | Total
Virus | 5-log | -- | -- | -- | 6-log | 2-log | 13-log
Giardia | 2.5-log | -- | 4-log | -- | 6-log | -- | 12.5-log
Cryptosporidium | -- | -- | 4-log | -- | 6-log | -- | 10-log
OZONE
BAF
UF
GAC
UV
Cl2
Virus
Giardia
Crypto
12-log
10-log
10-log

## Slide 45: Alternative Treatment Trains (The subject of the new CEEN 471)

## Slide 46: So…, where the data is coming from…?
Online continuous measurements:
  Flow, pressure, level, temperature, conductivity, pH, turbidity (including TSS), ORP, oxygen (DO), TOC, specific ions (ammonia, nitrate, chlorine, hardness, etc.), state
  Sensor vs. analyzer!
Lab analysis
  Metals (ICP), anions (IC), radionuclides, organic micropollutants (LC, GC), VOCs, O&G, microbial community, surface charge & morphology,

## Slide 47: Thank you
~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~
Tzahi Cath, Ph.D.
Professor and AQWATEC Director
COLORADO SCHOOL OF MINES
Department of Civil and Environmental Engineering
1500 Illinois St., Golden, Colorado 80401-1887
Office: 303.273.3402
Email: tcath@mines.edu
Cath URL: http://inside.mines.edu/~tcath/
AQWATEC URL: http://aqwatec.mines.edu/
ERC URL: http://urbanwatererc.org/
CEE URL: http://cee.mines.edu/
~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~